## BOQ FOR GRP TANK&TOWER
SUPPLYING, AND TRANSPORTATION OF A GLASS REINFORCED PLASTIC (GRP) TANK & TOWER WITH CAPACITY OF 31944 LITER
ITEM | DESCRIPTION | UNIT | QTY | RATE | AMOUNT
|  |  |  | (USD) | (USD)
1 | Supply Glass reinforceed Plastic (GRP) water Tank of 31944 Cubic meter capacity. | Pc | 1
The Tank shall be made from Molded Glass Reinforced Fiber/ Synthetic Material Composite (SMC) Panels designed from resins conforming to BS 3532 specifications and fiberglass conforming to BS 3749 specification
The sizes of panels shall be 1220mm x 1220mm that are molded from a Glass Reinforced Fiber/ Synthetic Material Composite (SMC) Panels designed from resins
The thickness of panels shall be 5mm.
External materials shall be SS304/SS316 Stainless Steel Bolts, Nuts, Washers, SS304/ SS316 Stainless Steel Ladder, PVC Air Vents, Water Level Indicator, and Manhole Cover
Internal materials shall be SS304/SS316 Stainless Steel Bolts, Nuts, Washers, Tie Rods, Bracing Plates, PVC Vertical Supports and SS304/SS316 Stainless-Steel Ladder.
Food-grade rubber (Silicon EPDM) and sealant shall be used to join the panels and flanges
Pressed panel steel tank shall be design to carry water of a density 1000Kg/m3.
The out-let sizes of 75mm shall be design on the site way panel of the tank, 100mm above the tank based and shall be on the site of primary beam.
Two 2 Wash out-let sizes of 75mm shall be design on the bottom (Based) panel of the tank
The In-let sizes of 50mm shall be design on the top panel of the tank.
| Supply of rust protection paints, one coat of Non-toxic Zinc Phosphate Primer (2 Tins of 4 liters) and two coats Non-toxic Black Bituminous Paint (3Tins of 4 liter) | 5TINS
LMS
2 | Supply of Tower capable of holding 31944 Tank Capacity
Supply of steel Tower I/H columns beam 6No. of 6-meter height, and shall be 150mmx 200mm x 6000mm height
The I/H columns steel Beam thickness shall be 8mm
The Horizontal Primary and secondary beams shall be I/H steel Beam of 200mm weight x 100mm length with thickness of 6mm
RSA diagonal bracing of 75mm x 75mm and shall have a thickness of 4mm
Platform fabricated using steel-beams, 2.1mm thick chequered plate, 610mm wide perimeter walkway, 900mm high hand-railing, and tower fabricated out of columns, bracings, cat-ladders, and bolts
3 | Transportation cost of materials to WFSSF warehouse in Wau, South Sudan
GRAND TOTAL